## Sheet2
Model（HP） |  |  | 3 | 4 | 4.5 | 4 | 5 | 6 | 4.5 | 5 | 6 | 8 | 10 | 12 | 8 | 10 | 12
Model |  |  | AVW-28HJFH | AVW-34HJFH | AVW-43HJFH | AVW-38HJFH | AVW-48HJFH | AVW-54HJFH | AVW-43HKFH | AVW-48HKFH | AVW-54HKFH | AVW-76HKFH | AVW-96HKFH | AVW-114HKFH | AVW-76H9FH | AVW-96H9FH | AVW-114H9FH
Power Supply |  | - | 220-240V ~ 50/60Hz | [5 empty] | 380-415V 3N～ 50/60Hz | [5 empty] | 220V 3～ 60Hz
Cooling Operation | Nominal Capacity | Btu/h | 27300 | 34100 | 42700 | 38200 | 47800 | 52900 | 42700 | 47800 | 52900 | 76500 | 95600 | 114300 | 76500 | 95600 | 114300
|  | kW | 8 | 10 | 12.5 | 11.2 | 14 | 15.5 | 12.5 | 14 | 15.5 | 22.4 | 28 | 33.5 | 22.4 | 28 | 33.5
| Power Consumption | kW | 1.93 | 2.34 | 2.98 | 2.6 | 3.46 | 4.21 | 3.81 | 3.92 | 4.44 | 6.36 | 7.8 | 10.6 | 6.3 | 8.3 | 10.7
| EER |  | 4.1451 | 4.2735 | 4.1946 | 4.3077 | 4.0462 | 3.6817 | 3.2808 | 3.5714 | 3.491 | 3.522 | 3.5897 | 3.1604 | 3.5556 | 3.3735 | 3.1308
Heating Operation | Nominal Capacity | Btu/h | 32400 | 38200 | 47800 | 42700 | 54600 | 61400 | 47800 | 54600 | 61400 | 85300 | 107500 | 128000 | 85300 | 107500 | 128000
|  | kW | 9.5 | 11.2 | 14 | 12.5 | 16 | 18 | 14 | 16 | 18 | 25 | 31.5 | 37.5 | 25 | 31.5 | 37.5
| Power Consumption | kW | 2.37 | 3.01 | 4.15 | 2.78 | 3.71 | 4.47 | 3.68 | 4.03 | 4.74 | 5.81 | 7 | 10.11 | 5.9 | 7.8 | 9.9
| COP |  | 4.0084 | 3.7209 | 3.3735 | 4.4964 | 4.3127 | 4.0268 | 3.8043 | 3.9702 | 3.7975 | 4.3029 | 4.5 | 3.7092 | 4.2373 | 4.0385 | 3.7879
Cabinet Color |  | - | Ivory White
Sound Pressure Level （Cooling/Heating） |  | dB(A) | 50/52 | 53/55 | 54/57 | 50/52 | 52/54 | 53/55 | 55/57 | 48/50 | 50/52 | 58/60 | 59/61 | 59/61 | 53/55 | 56/58 | 56/61
Out Dimension(H×W×D) |  | mm | 800×950×370 | 800×950×370 | 800×950×370 | 1380×950×370 | 1380×950×370 | 1380×950×370 | 800×950×370 | 1380×950×370 | 1380×950×370 | 1650×1100×390 | 1650×1100×390 | 1650×1100×390 | 1650×1100×390 | 1650×1100×390 | 1650×1100×390
Packing Dimension(H×W×D) |  | mm | 930×1025×460 | 930×1025×460 | 930×1025×460 | 1520×1025×460 | 1520×1025×460 | 1520×1025×460 | 930×1025×460 | 1520×1025×460 | 1520×1025×460 | 1748×1151×500 | 1748×1151×500 | 1748×1151×500 | 1748×1151×500 | 1748×1151×500 | 1748×1151×500
Net Weight |  | kg | 65 | 73 | 78 | 93 | 95 | 97 | 84 | 103 | 103 | 160 | 170 | 170 | 168 | 168 | 171
Gross Weight |  | kg | 72 | 81 | 86 | 111 | 111 | 111 | 96 | 118 | 118 | 179 | 194 | 194 | 179 | 179 | 182
Refrigerant Category |  |  | R410A
Refrigerant Flow Control |  |  | Micro-Computer Control Expansion Valve
Compressor |  | Model | Hitachi(Rotary) | [5 empty] | Hemetic(Scroll)
|  | Quantity | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Drive Mode | DC
Refrigerant Oil Type |  |  | α 68HES-H | [5 empty] | FVB68B
Heat Exchanger |  |  | Multi-Pass Cross-Finned Tube
Condenser Fan |  | Model | Propeller Fan
|  | Quantity | 1 | 1 | 1 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  | Drive Mode | DC
Air Flow Rate |  | m3/min | 46.5 | 69 | 78 | 90 | 90 | 100 | 75 | 90 | 100 | 150 | 163 | 163 | 121 | 150 | 163
Motor Output(Pole) |  | kW | 0.051（8） | 0.138（8） | 0.138（8） | 0.051（8） | 0.051（8） | 0.051（8） | 0.138（8） | 0.051（8） | 0.051（8） | 0.138（8） | 0.138（8） | 0.138（8） | 0.138 | 0.138 | 0.138
Connections |  |  | Flare-Nut Connection(With Flare Nuts)
Refrigerant Piping | Liquid Line | mm(in.) | Φ9.53(3/8) | Φ9.53(3/8) | Φ9.53(3/8) | Φ9.53(3/8) | Φ9.53(3/8) | Φ9.53(3/8) | Φ9.53(3/8) | Φ9.53(3/8) | Φ9.53(3/8) | Φ12.7(1/2) | Φ12.7(1/2) | Φ12.7(1/2) | Φ9.53(3/8) | Φ12.7(1/2) | Φ12.7(1/2)
| Gas Line | mm(in.) | Φ15.88(5/8) | Φ15.88(5/8) | Φ15.88(5/8) | Φ15.88(5/8) | Φ15.88(5/8) | Φ15.88(5/8) | Φ15.88(5/8) | Φ15.88(5/8) | Φ15.88(5/8) | Φ22.2(7/8) | Φ25.4(1/1) | Φ25.4(1/1) | Φ19.05(3/4) | Φ22.2(7/8) | Φ25.4(1/1)
Refrigerant Charge(before shipment) |  | kg | 2.5 | 2.8 | 2.8 | 3.8 | 3.8 | 4.1 | 3 | 3.6 | 3.6 | 7 | 9 | 9 | 5 | 5.5 | 6.5
Max. number of connectable IDU |  |  | 5 | 6 | 8 | 9 | 11 | 11 | 8 | 11 | 11 | 15 | 17 | 19 | 10 | 10 | 10
Matching range |  |  | 50%~125% |  |  | 50%~150% |  |  | 50%~125% | 50%~150% |  |  |  |  | 50%~130%
Max. Piping Length |  | m | 25 | 25 | 50 | 75 | 75 | 75 | 50 | 75 | 75 | 100 | 100 | 100 | 100 | 100 | 100
Height Difference | Between ODU & IDU | m | 20 | 20 | 20 | 30 | 30 | 30 | 20 | 30 | 30 | 40 | 40 | 40 | 40 | 40 | 40
| Between IDUs | m | 3.5 | 3.5 | 3.5 | 10 | 10 | 10 | 3.5 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
Operation Range | Cooling | ℃ DB | -5~46
| Heating | ℃ WB | -15~15.5 |  |  | -20~15.5 |  |  | -15~15.5 | -20~15.5
Branch pipe |  |  | HFQ-052F | [8 empty] | HFQ-162F |  |  | HFQ-102F（*1） | HFQ-162F
Approximate Packing Measurement |  | m3 | 0.44 | 0.44 | 0.44 | 0.874 | 0.874 | 0.874 | 0.44 | 0.874 | 0.874 | 1 | 1 | 1 | 1 | 1 | 1
*1）When the euquvalent piping length is less than 70m, the first branch is HFQ-102F, or the first branch is HFQ-162F.
Note: 1.The nominal cooling capacity and hesting capacity are based on following conditions: Cooling Operation Conditions Heating Operation Conditions Indoor Air Inlet Temperature:27.0℃ DB（80°F DB） Indoor Air Inlet Temperature:20℃ DB（68°F DB） 19.0℃ DB（66.2°F DB） Outdoor Air Inlet Temperature:35.0℃ DB（95°F DB） Outdoor Air Inlet Temperature:7℃ DB（45°F DB） 6℃ DB（43°F DB） Piping Length:7.5Meters Piping Lift:0Meters 2.The sounf pressure level is based on following conditions: 1.5m beneath the unit. The above data was measured in an anechoic chamber so that reflected sound should be taken into consideration in the field. 3.When the cooling operation temperature is over 46℃, please contact our professional engineer.