## Slide 1
Hi Dom Ⅲ Control System
Eason Xiao

## Slide 2
Introduction
01
02
Main Functions
03
Principle
04
Note

## Slide 3
1
Introduction

## Slide 4
Introduction
Connection Diagram

## Slide 5
Introduction
Hi-Dom III Air Conditioning Management System
Hi-Dom III air conditioning management system adopts communication bus connection, air conditioning indoor units are connected to the computer through network converter. The system is all controlled automatically by a computer with powerful functions and simple operation. In accordance with the operation time and capacity output of indoor and outdoor units, the electric charge allocation software allocates the total power consumption to each indoor unit.

## Slide 6
HCCS-H160H2C1NM
HCCS-H160H2C1YM
Hi-Dom III adapter
Centralized control, without charging function
Centralized control, with charging function
Max. connectable IDUs of one Hi Dom III | 160
Max. connectable ODUs of one Hi Dom III | 64
Max. connectable meters of one Hi Dom III | 64
Max. adapters one computer can connect | 32
Max. total connectable IDUs | 5120
Introduction

## Slide 7
Hardware：
System Component | Parameter Requirements | Demand Quantity | Offer
Hi-Dom III | HCCS-H160H2C1YM | 1 per 160 IDUs | Hisense
Software | — | 1 per management computer | Hisense
Management Computer | — | 1 per project | Provided on-site
Control Box | Including power source and HUB | — | Provided on-site
Electric Meter | Schneider meter | 1 per ODU | Designated manufacturer
Introduction

## Slide 8
Hi-Dom III adapter is used in the system to converse the communication, record the running data and read the meter data.
Introduction
Item | Specifications
Power supply | DC 12V
Power consumption | <6W
Environmental conditions | Ambient temperature: 0～40℃
 | Ambient humidity: 20～85% (no condensation)
Dimensions | Length: 180mm, Width: 115mm, Thickness: 64mm
Weight | 0.57kg
Installation conditions | Indoor, weak current control box; rail or lifting hole fixed

## Slide 9
Dimension
Introduction

## Slide 10
Computer configuration
Management Computer
Introduction
Hardware | CPU: i5-6th generation and above Memory: 8GB and above HDD: 500GB and above NIC: 1.0Gbps, RJ45 interface Display: resolution should be 1920*1080.
Software | Operating system: Win10 or Win7 64bit Browser: Google Chrome, 64bit, version 65 and above Application software: Excel 2007 and above

## Slide 11
A management computer adapts and save the data conversed by Hi-Dom adapter, adapts the meter data and make the calculation of the household charging.
Management Computer
After installing the software, the industrial computer become the monitoring server.
The server supports multi-user simultaneous access on the local area network.
Introduction

## Slide 12
Electric meter
Schneider iEM3150
Schneider iEM3250
Selection suggestion |  | 
Max Running Current (A) | ≤55 | ＞55
Model | iEM3150 /3155 | iEM3250 /3255 Used with transformer
Introduction

## Slide 13
2
Main Functions

## Slide 14
Main Functions
■Running State Monitoring
■Running Data Record
■Determine Temperature Limit
■3 Levels Account Authority
■Controller Prohibition Function
■Schedule Setting
■Multifunction Alarm
■Electric Charge Allocation
■External Input & Output
■2D Navigation

## Slide 15
User Selected
Main Functions
Monitor & Control (big tags)
Big tag
Small tag
List
Up to 60 indoor units can be displayed in one page.
Notes: 设定内容和室内机功能、是否连接线控器有关系

## Slide 16
Main Functions
Monitor & Control (small tags)
Up to 300 indoor units can be displayed in one page.

## Slide 17
Main Functions
Monitor & Control (list tags)
Up to 600 indoor units can be displayed in one page.

## Slide 18
Timer management
Main Functions

## Slide 19
Main Functions
2D Navigation

## Slide 20
Main Functions
Electric Consumption Allocation
Post Payment:
Using AC → Usage report → Charging the tenants
Pre Payment:
Recharge → Using AC → A reminder when the balance is insufficient → ◌ Can choose to switch off and lock AC when in arrears
The prices of max. 5 time periods can be set. Time period starts from 00:00 and the last one is until 24:00 by default.

## Slide 21
Main Functions
Electric Consumption Allocation (Post Payment)
The result can be exported to excel or pdf format.

## Slide 22
Main Functions
Electric Consumption Allocation (Pre Payment)
The result can be exported to excel or pdf format.
Notes: 预付费扣费原则 以一天作为结算周期，在每天1点对前一天的电量进行结算并扣费。 如果某用户扣费后的余额如果低于设定的“余额不足提示”，软件将对该用户下所有室内机弹出余额不足的提示； 如果某用户扣费后的余额小于0，软件将对该用户下所有室内机（同一个线控器组的从机除外）每隔1小时发出一次关机&控制锁定的命令（选择了欠费强制关机的前提下），并弹出欠费停机的提示。

## Slide 23
Main Functions
AC Running Data
The result can be exported to excel format.

## Slide 24
Main Functions
AC Running Data (excel content example)

## Slide 25
Main Functions
Running Statistics
The result can be exported to excel format.

## Slide 26
Main Functions
Alarm record
The result can be exported to excel format.

## Slide 27
Main Functions
Energy saving

## Slide 28
Main Functions
3 Levels Account Authority
① admin1:
Have the highest administrative authority.
② admin:
Adv. Management menu is unavailable. Authorities are set by admin1.

## Slide 29
Main Functions
3 Levels Account Authority
③ user + n:
Only the indoor units under this user can be displayed. Available menus: Monitor & control, 2D navigation, timer management (view task). Authorities are set by admin1.

## Slide 30
Main Functions
Remote control
Cloud service technology is under development in the factory. However, the Hi Dom III management system supports remote control with intranet penetration or VPN technology.

## Slide 31
3
Principle

## Slide 32
Principle
Electricity Consumption
Compressor
Fan motor
Electric heating belt
Standby electricity: If all the indoor units connected by an outdoor unit are not running for a period of time, the electric energy consumed by the electric heating belt is called the standby electricity.
Fan motor
IDU
ODU
Eo
Es
Ei
Meter

## Slide 33
Principle
IDU
ODU
Eo
Es
Ei
Eo: Electricity consumption of ODU running
Calculated per hour
Es: Standby electricity
Calculated per day
Eo: Electricity consumption of IDU running
Calculated per hour

## Slide 34
Principle
ODU
Eo
Eo: Electricity consumption of ODU running
Calculated per hour
The system takes the
indoor unit running status,
the running time and
the opening value of the electronic expansion valve as the distribution basis to allocate Eo to every indoor unit.
IDU1
IDU2
IDU3
IDU4
Eoi1
Eoi2
Eoi3
Eoi4

## Slide 35
Principle
Es
Es: Standby electricity
Calculated per day
Electric heating belt
Choice 1:
Allocated to the indoor units in use. The same calculation as the Eo allocation. However, if the outdoor units are in standby all the day, the software will allocate the Es to the management cost automatically.
Choice 2:
Divided to the management cost.
IDU1
IDU2
Esi1
Esi2
Or
Es
Management cost

## Slide 36
KWh
Public Electric Meter
Public Lighting
IDU 01
IDU 02
Public Electricity
Principle
Indoor Unit Electricity Consumption Method 1
Estimated by Hi Dom III system
Or
Divided into the management cost
IDU
Ei

## Slide 37
KWh
Tenant Electric Meter
Lighting
Kitchen and Toilet Socket
Spare
Indoor Power Distribution Box
Socket
IDU
Principle
Indoor Unit Electricity Consumption Method 2
No need for calculation in our control system.

## Slide 38
Principle
Indoor Unit Electricity Consumption Method 3
KWh
Electric Meter
ODU
IDU 01
IDU 02
SW BOX
Measured and calculated together with ODU in the same system

## Slide 39
Principle
Electricity consumption of public and idle indoor units
Public: Indoor units installed in public areas.
Idle: Indoor units that are idle while the users are not found.
In use: Indoor units that are rented by users.
Choice 1:
Allocated to the indoor units averagely which are connected to adapters with charging allocation function and in use.
Choice 2:
Divided to the management cost.

## Slide 40
Principle
Summary
Electricity Usage of tenant
Et = ∑ Eis
Eis = Eoi + Esi +Ei + Epi
Em = Es + Ep
Eis, the total electricity consumption allocated to one indoor unit.
Eoi, the electricity consumption allocated from ODU running electricity.
Esi, the electricity consumption allocated from standby electricity.
Epi, the electricity consumption allocated from public and idle indoor units.
Em, the management cost.
Es, the standby electricity.
Ep, the electricity consumption of public and idle indoor units

## Slide 41
4
Note

## Slide 42
Note
The power supply of indoor units should be switched together by property manager.
If the power supply is controlled by tenants, it may lead to condensate water because the EEV may remain open when the IDU is cut off. And the AC system wouldn’t work when the ratio between IDUs and ODU is less than 50%.

## Slide 43
Note
2. The allocated electricity consumption for two same model IDUs in the adjacent rooms will be different.
According to the operating time of the air conditioning indoor units, the electronic expansion valve and the capacity of the indoor units, the control system assigns the power consumption of an outdoor unit in a refrigeration system to the indoor units. When the indoor cooling load is large (such as in the refrigeration, the indoor temperature is higher, the door and window is open, the setting temperature is low), the electronic expansion valve opening degree will also become larger, so the air conditioning users share the electric charge will be different.

## Slide 44
Note
3. The allocated electricity will be large when the IDUs operation rate is low.
Scene 1, total 10HP IDUs are switched on in a 50HP AC system. (Similar scene happens commonly in apartment building project)
Scene 2, total 30HP IDUs are switched on in a 50HP AC system.
Assume that there is a 2HP IDU operating in the same condition in both scenes separately. The allocated electricity for the 2HP IDU scene 1 will be larger than the one in scene 2.
We recommend that you should design the air conditioning systems as small as possible if low IDUs operation rate always happens.
IDUs Operation Rate
ODU Power Consumption
50%
100%

## Slide 45
Note
4. If you need to use the Electricity consumption allocation function, the computer with the host software installed must run continuously around the clock.
4.1. Ensure that the software is always running in the background;
4.2. Ensure that the operating system has turned off the sleep mode.
4.3. To prevent abnormal power failure, it is recommended to install the UPS.
Recommended UPS specifications: 1000VA/600W and above.

## Slide 46
THANKS